*************************************************************************************************************************

ÖFFENTLICHE AUSSCHREIBUNG / PUBLIC ANNOUNCEMENT

Replacing AHU and install of cooling system

**************************************************************************************************************************

The U.S. Consulate General Frankfurt invites you to submit offers for a firm fixed price for:

Das US Konsulat Frankfurt bittet Sie ein Pauschalangebot für die folgenden Leistungen zu übermitteln:

I.	GENERAL INFORMATION

This Statement of Work is intended to identify basic requirements for the installation of HVAC controls and cooling coil(s) in an air handling unit at the U.S. Consulate Frankfurt, and to provide applicable criteria, which the Contractor must use, for the preparation of work.

II.	PROJECT REQUIREMENTS

- Description of Project:

The United States Government (USG) Department of State (DOS), Consulate Frankfurt is planning the replacement of antiquated solid state controls on an existing Air Handling Unit in the COB. Furthermore, the installation and integration of cooling coils with corresponding external compressor and condenser. The new controls should encompass all existing data points and include the actuation of cooling in respect to room temperature set points. A room thermostat will be installed to monitor room temperature and the new controls and software will balance heating, ventilation and air conditioning based on this value. New controls will be compatible for integration into an existing third party BACNET building automation system.

B.	General Requirements:

- The work requires construction services as described herein.

- The Contractor will be responsible for the engineering of the replacement HVAC controls and cooling system integration and such planning will be included in the bidding price.

3.	The Contractor shall maintain a system of quality assurance and quality control	to ensure that the documentation of the design meets the requirements of this contract.

4.	The Contractor will be responsible for labor, tools and materials required to carry out the work outlined in this SOW.

5.	The Contractor will be provided with existing floorplans and mechanical drawings where available.

- Specific Requirements:

Planning and Installation

  - Preparation:

Identify all existing data points to be controlled by the main controller.

Verify that all actuation and sensing devices are compatible with the new proposed control package.

Create a concrete plan of cooling integration and verify that all components will fit and function as required to supply sufficient cooling for space in question.

Identify location of control cabinet and mounting strategy

Identify location of external compressor / condenser unit

Identify method of hot air exhaust from attic space (louvre or exhaust air duct retrofit).

  - Removal:

Removal of old controls and components or infrastructure deemed unusable. Insure proper disposal of removed equipment.

  - Retrofit:

Retrofit existing AHU duct for integration of cooling coils

Ensure installation is mechanically sound and visually acceptable.

Retrofit of exhaust air duct (when deemed possible) for hot

air exhaust from cooling condenser unit or install exhaust fan to

remove heat from condenser unit from attic space.

1.4 Installation work:

Adhere to all regulations governing the installation of HVAC

equipment and controls.

Install new cooling coil, compressor, condenser and actuators

Install new control cabinet and controls

Connect all cables

Ensure installation is sound, safe and in accordance with local regulations and codes and professional in appearance.

Mark all cables and identify all data points in a clear and

understandable schematic drawing.

1.5 Controls and Software:

Install industry standard controls and software with English

language capability

Software should be BACNET compatible for integration into

existing building automation system for monitoring.

- Construction Documents:

  - The Contractor shall produce project contract plans and technical

drawings as required.

  - All floorplans or mechanical drawings supplied to or created by the contractor are property of the US Government and shall be returned to the Contract Officer Representative (COR) upon completion of the Project.

  - Schematic diagrams shall be created identifying all data points and components in a clear and understandable manner.

  - Operations and Maintenance manuals shall be provided explaining control and software program adjustments.

## E.	Special Requirements:

1.	The Contractor shall be Responsible for obtaining local information, translating documents, etc.  The Contractor's proposal shall reflect the cost and extent of these services as determined by the Contractor, to be required.  The Contractor shall be responsible to see that the work will be constructed with materials, finishes, equipment and systems that provide operational dependability and are easy to maintain or replace with those most readily available supplies and services.  Emphasis must be placed on the uniformity of parts and components to maximize interchangeability.

- The Contractor shall provide Quality Assurance certificates or equivalent documents for all materials and equipments to be used.

- The Contractor will be required to have at least one Technician complete necessary background check paperwork.

- The Contractor shall provide specific operations and maintenance data and information on equipment installed.

- The contractor shall provide in service testing and operation and maintenance training to facilities personnel.

#### III.	CODE COMPLIANCE

A.	All designs/work performed must comply with the German Standards according to the different Codes which are given for installation and operation of air handling units, construction safety practices and environmental issues.  Inconsistencies shall be brought to the COR's attention in writing.  The COR will resolve any inconsistencies.

B.	Project Schedule:

The Contractor shall develop a construction schedule to minimize the

Effect of  operations at COB. Such schedule shall be coordinated with and approved by the COR.

IV.	INSPECTION

A.	The Contractor shall maintain a system of quality assurance and quality control to ensure that the documentation of the design meets the requirements of this contract.  The Government reserves the right, as provided herein, to inspect the Contractor's work as well as his system of QA/QC.

V.	ACCEPTANCE

- Acceptance of deliverable items shall be by the Contracting Officer's Representative.  Acceptance or use of documents developed under this contract shall not in any way relieve the Contractor of responsibility for the design.

CONCEPT DRAWING

Site visit:

Besichtigungstermin:

6. September, 2018, 9:00 (Bitte mind. 48 Stunden im Voraus bestätigen)

Payment terms:

Zahlungsbedingungen:

Payment terms are to be 30 days after Government acceptance of supplies delivered/

Rechnungsstellung nach Lieferung mit 30 Tagen Zahlungsziel

Request for Quotation Number:

Ausschreibungsnummer:

PR7617704

Due date for quotation:

Letzter Abgabetermin:

17 September, 2018

The responsible purchasing agent for this announcement would be:

Der zuständige Ansprechpartner für diese Ausschreibung ist:

Purchasing Agent:  Thomas Petersen

E-Mail: FrankfurtGSOProcurementTeam@state.gov

**************************************************************************************************************************