SCOPE OF WORKS

NOB WALK IN COLD STORE/FREEZER REPLACEMENT

OVERVIEW

Client:

The United States Government (USG), Department of State (DOS), has a requirement to replace walk in cold store/walk in freezer

Location/Contacts: NEC/NOB 1st floor.

COTR (Contracting officer technical representative): Ruheni Peter C +254 0713600838 for the purpose of quality control, operational facilitation, technical review, project monitoring and evaluation.

OBJECTIVE

Requirements in this SOW serve as a direction to the Contractor undertaking replacement of freezer and cold store in NOB 1st floor. (Gents and Ladies toilets). The Contractor shall perform all services in accordance with local and international safety and construction standards as generally applicable to accepted professional practices. The work shall be undertaken according to the list specifications. No variations /deviations will be implemented without prior approval from contracting officer (CO). Any foreseeable element likely to warrant cost adjustments must be discussed at the point of quotation.

TIME FRAME

Upon receipt of the order, the contractor shall be expected to submit work plan/Work break down, resource allocation ( tools, labor, materials, equipment…), time schedule (Gantt Chart),  through the COTR within 5 days, commence work within 7 days and must undertake the work as per the agreed upon schedule.

APPLICABLE STANDARDS

1.	Local Building codes: the local government (adoptive by-laws)

(Building) order 1968

2.	Local Safety regulations: OSHA 2007 (safety compliance)

3.	Nairobi city Council by laws (operational compliance)

4.	NEMA by-laws (in safe disposal of waste)

5.	US safety regulations: US Army corps of Engineers

SPECIAL REQUIREMENTS

Access into the USG premises is at the discretion of the Regional Security office and therefore approval must be obtained at least 24hours before date entry. Work must be done under escort of the appropriate clearance level as applicable in the space concerned.

SCOPE OF WORK

| # | Description | units | Quantity |
| --- | --- | --- | --- |
| 1 | Provide labor, materials, tools and equipment , mobilize site and undertake complete walk in cold store replacement with unit of the following specifications: Chamber: Cold store space of at least 30 meter cubic with 100mm raised/ramped floor made of food grade /corrosion resistant stainless steel/Aluminum panel work. The floor shall be 5mm chequared plate . Install cold store door fitted with door heaters, lock, hinges, double walled inspection window. Indoor unit: Install unit of 48000 BTU cooling capacity evaporator with 4 fans powered by single phase 240V/50Hz power. The coil shall be made of food grade aluminum fins, with heater defrosts features, drains, thermostatic expansion valve, high wall mounted. Outdoor unit: Install 48000 BTU cooling capacity condensing unit powered using 415V/50Hz/3 phase power, with semi hermetic compressor. The Freon must be current as per international regulations. Allow all relevant features to allow installation of the unit 15m above the evaporator. Control panel: Install control panel complete with system protection, user safety, power saving features, panel and remote displays, alarm, fault indicators, PLC integrations with digital and analogue inputs/out put provisions. | Lump sum | 1 |
| 2 | Provide labor, materials, tools and equipment , mobilize site and undertake complete Walk in Freezer store replacement with unit of the following specifications: Chamber: Cold store space of at least 25 meter cubic with 100mm raised/ramped floor made of food grade /corrosion resistant stainless steel/Aluminum panel work . The floor shall be 5mm chequared plate . Install cold store door fitted with door heaters, lock, hinges, double walled inspection window. Indoor unit: Install unit of 48000 BTU cooling capacity evaporator with 3 fans powered by single phase 240V/50Hz power. The coil shall be made of food grade aluminum fins, with heater defrosts features, drains, thermostatic expansion valve, high wall mounted. Outdoor unit: Install 48000 BTU cooling capacity condensing unit powered using 415V/50Hz/3 phase power, with semi hermetic compressor. The Freon must be current as per international regulations. Allow all relevant features to allow installation of the unit 15m above the evaporator. Control panel: Install control panel complete with system protection, user safety, and power saving features, panel and remote displays, alarm, fault indicators, PLC integrations with digital and analogue inputs/output provisions. | Lump sum | 1 |
|  | Install stainless steel (food grade) shelves of the size as per the existing. | Lump sum | 1 |

TECHNICAL PROPOSALS EVALUATION

- Prior Experience and Past Performance.

The offeror shall demonstrated record, as confirmed by references, of successful past performance of the same or substantially similar contract efforts, including quality of services or supplies, timeliness of performance, cost control, and the offeror’s business relations.

- Qualifications of Key Personnel.

The key personnel assigned to the project possess relevant prior experience, special training and education

- Technical, Resource and Management Capability.

Offeror shall demonstrate the technical excellence, management and resource capability as required to successfully completing the project work.

- Execution plan and Quality control:

The contractor shall demonstrate that he/she understands the Scope Of Work (SOW) clearly, has a technically feasible plan to execute the project as per SOW and has quality control plan. The project tasks must be broken and presented in a work schedule not exceeding 4 weeks.

- Material Specifications:

The offer shall provide material data sheet for the materials required as proof of satisfaction of material specifications