THE UNITED STATES OF AMERICAN EMBASSY RABAT, MOROCCO

Preventive Maintenance and Repair Services for NEC Elevators

STATEMENT OF WORK

- INTRODUCTION:

The contractor agrees to provide monthly comprehensive preventive maintenance, repair and communications program for five (5) OTIS brand elevators at the American Embassy in Rabat:

| Sl.No | Lift reference | Machine No. | Duty Load (kg) | Speed (m/s) | Stops |
| --- | --- | --- | --- | --- | --- |
| 1 | Passenger Elevator | NGH465 | 1800 | 1 | 3 |
| 2 | Passenger Elevator | NGH466 | 1800 | 1 | 3 |
| 3 | NOB Service Elevator | NGH467 | 2000 | 1 | 5 |
| 4 | Staff Parking Elevator | NGH468 | 2000 | 1 | 4 |
| 5 | Official Parking Elevator | NGH469 | 1800 | 1 | 3 |

- SCOPE OF SERVICES:

Contractor shall provide skilled, competent employees and trained by the elevator manufacturer or an accredited elevator apprentice program for the purpose of maintenance and repair of elevators to ensure safe and reliable operation of the equipment. Maintenance shall include monthly preventive maintenance, repair and replacement of worn or defective components, lubrication, cleaning, and adjusting as required for operation as designed. Only parts and supplies recommended by the original equipment manufacturer shall be installed.

- GENERAL WORK REQUIREMENTS

The Contractor shall provide full service to meet routine maintenance requirements.  The Contractor shall maintain elevators so that the elevators are in a safe and efficient operating condition at all times.  In the event of a break down, the Contractor shall make every effort to immediately return the elevator to an operating condition.

Contractor will carry out repairs including the replacement of like for like parts, where such repairs are due to normal use, as listed below:

- Worms/gears, sheaves,  bearings, Motors, brake coils and windings and for the machine (excluding complete replacement);

- Relays, electronic boards (PCB) and contacts for the controller and drive system;

- Main hoist ropes  and over speed governor ropes;

- Governor component (excluding complete governor replacement);

- Guide shoes/rollers and safety gear;

- Locks and their actuating elements;

- Door operators including their motors and contacts;

- Car door hangers, door shoes and tracks.

- Position indicators(excluding LCD displays/indicators) and buttons

- MINIMUM REQUIREMENTS:

The Contractor shall provide a trained mechanic to inspect and service every elevator a minimum of, once a month, every month of the year.  The elevator mechanic shall sign off on every item of the checklist.  The elevator mechanic shall leave a copy of this signed checklist with the COR or the COR's designate following that month's routine maintenance visit.  This weekly inspection and servicing shall include, but not be limited to, the following tasks:

- Ride all cars to detect and repair any improper operation of the car doors, hoistway doors, acceleration, leveling accuracy on the floor stops, and the action of the machine brake;

- Check and make necessary repairs to assure proper operation of retractable doors;

- Review elevator’s performance with the COR, or the designated representative, to determine if any malfunctions have occurred in connection with the operation of the cars since the most recent previous scheduled routine maintenance visit;

- Investigate any malfunctions which have occurred, devoting special attention to any problem involving unsafe operations, and make repairs as necessary;

- Examine car stations and call buttons and replace any damaged switches, burned out lamps, bulbs and broken buttons, defective fixtures, switches, covers, and related hardware;

- Troubleshoot any failure to equipment, lighting and receptacle electrical circuits;

- RESPONSIBILITIES OF THE CONTRCATR:

All service operations are provided by specialist technicians trained and certified in the maintenance and repair of OTIS elevators.  Technicians must have continual training programs and the assistance of regional, national and international experts ensuring OTIS standards.

Contractor shall provide 24 hours breakdown service. Contractor shall maintain a day and night 24 hour service to respond to emergencies. If the break down is not due to a reason other than the normal use of equipment, the service corresponding to the call will be charged as an addition to this contract.

Local service offices must have access to maintenance service center support with access to urgent delivery of parts and components ensuring maximum availability of the equipment.

Contractor shall provide a detailed report upon request, covering both equipment breakdown report and the finding and recommendations of any quality and safety audits.

During each visit, the technician collects information regarding the functioning of the lift 	and informs the customer representative in the building of the work undertaken. If a breakdown cannot be repaired in a single visit, before leaving the site the technician will provide the plan for returning the elevator to normal service.

Contractor shall provide timely proposals on the modernization of the equipment and obsolete parts to enhance performance, comfort, energy saving, aesthetics, and to reduce pollution together with anticipated measurable benefits, such as modernization/upgrade costs are excluded from this contract.

Insurance Coverage - Throughout this service contract, contractor shall cover the workmen compensation liability for its employees and third party liability relative to its work.

Personnel, Tools, Repair Parts, Materials and Supplies: The Contractor shall provide trained elevator mechanics with the appropriate tools and testing equipment for scheduled maintenance, unscheduled repairs, emergency repairs/assistance, safety inspection, and safety testing as required by this contract.  The Contractor shall provide all of the necessary repair parts, materials and supplies to maintain, service, inspect and test the elevators as required by this contract.

Callback Service: When an elevator which was previously worked on by the Contractor's mechanic, has a repeat malfunction within a 24-hour period, the Contractor shall be obligated to provide, at no extra cost, a return visit by a trained elevator mechanic to correct the problem, even if the problem is minor in nature.  The elevator mechanic shall respond to this callback within a three-hour time period regardless of what time the Contracting Officer or COR made the callback complaint, including the "after hours" time periods

- EXCLUSIONS:

The Contractor shall not assume responsibility for the following items of elevator 	equipment, which are not included in this contract:

- Car enclosures and related items including, but not limited to, fixed or removable panels, door panels, car gates, plenum chambers, hung ceilings, light diffusers, fluorescent tubes, dry cell batteries, handrails, mirrors, floor coverings, carpets and other architectural features and accessories;

- Buried caissons, cylinders and piping, and power supply feeder circuits to the machine room circuit breakers;

- Computer and microprocessor devices not exclusively dedicated to the elevator equipment such as terminal keyboards and display units;

- Communications equipment, such as telephones, intercoms, heat detectors, and smoke sensors, which were not installed by the Contractor or the original elevator installer;

- Major Repairs: Any individual unit or incident of repair with a total estimated cost (labor and direct material costs) exceeding $10,000.00 which is not covered under routine maintenance, is not covered by this contract.  The Government reserves the right to determine how these repairs are to be handled.  Such repairs will normally be accomplished by separate purchase order or contract.  This exclusion does not apply if the repair is to correct damage caused by Contractor negligence.

END OF THIS STATEMENT OF WORK