The U.S. Consulate in Ciudad Juarez, Chihuahua, Mexico is requesting quotes for fan coil units and chiller package installation as per product specifications below. Please send all quotes in Excel format no later than September 15th, 2017 at 4:00 pm (mountain time) to MaciasG@state.gov. No quotes will be considered after this date and time. For ALL vendors it is required that you have a current DUNS number and that you are registered in SAMs, no quotes will be considered without meeting these criterion. Mexican vendors must quote in pesos unless they have a U.S. Dollar bank account in Mexico. DUNS number on quote is mandatory.

Change of Split units Scope of Work

SUMMARY

U.S. Consulate Ciudad Juárez requests quotes for the purchase and installation of (3) new Split System Air conditioning units, installation, remove of all units installed and all the necessary accessories to have a functional system. Services to be performed include transportation and logistics of the equipment, installation and initial testing. Materials should be procured and services should be performed in accordance with below specifications:

DESCRIPTION

Split System Units that meet the following specifications:

- Split Unit

  - Service CAC

    - (1) Split system Heat Pump unit of 5 ton

    - 480v, 3 phase, 60 Hz

    - Refrigerant: 407

    - Remove existing unit

    - Modified base for new unit

  - Main CAC

    - (1) Split system Heat Pump unit of 5 ton

    - 480v, 3 phase, 60 Hz

    - Refrigerant: 407

    - Remove existing unit

    - Modified base for new unit

  - Consular CAC

    - (1) Mini Split system Heat Pump unit of 3 ton

    - 480v, 3 phase, 60 Hz

    - Refrigerant: 407

    - Add Base for the new

    - Repair penetrations at bituminous roof (pipes and base)

PRODUCTS

- CEILING-MOUNTING, EVAPORATOR-FAN COMPONENTS

  - Cabinet: Enameled steel with removable panels on front and ends in color selected by Contracting Agent, and discharge drain pans with drain connection.

  - Refrigerant Coil: Copper tube, with mechanically bonded aluminum fins, complying with ARI 210/240, and with thermal-expansion valve.

  - Electric Coil: Helical, nickel-chrome, resistance-wire heating elements with refractory ceramic support bushings; automatic-reset thermal cutout; built-in magnetic contactors; manual-reset thermal cutout; airflow proving device; and one-time fuses in terminal box for overcurrent protection.

  - Fan: Centrifugal fan, with power-induced outside air, and integral condensate pump.

  - Fan Motors: Comply with requirements in Division 15 Section "Motors."

  - Special Motor Features: Multitapped, multispeed with internal thermal protection and permanent lubrication.

  - Filters: Permanent, cleanable.

- AIR-COOLED, COMPRESSOR-CONDENSER COMPONENTS

  - Casing: Steel, finished with baked enamel, with removable panels for access to controls, weep holes for water drainage, and mounting holes in base. Provide brass service valves, fittings, and gage ports on exterior of casing.

  - Compressor: Hermetically sealed with crankcase heater and mounted on vibration isolation. Compressor motor shall have thermal- and current-sensitive overload devices, start capacitor, relay, and contactor.

    - Compressor Type: Reciprocating or Scroll.

  - Two-speed compressor motor with manual-reset high-pressure switch and automatic reset low-pressure switch.

  - Refrigerant Coil: Copper tube, with mechanically bonded copper fins, complying with ARI 210/240, and with liquid subcooled.

  - Heat Pump Components: Reversing valve and low-temperature air cut-off thermostat.

  - Fan: Aluminum-propeller type directly connected to motor.

  - Motor: Permanently lubricated, with integral thermal-overload protection.

  - Low Ambient Kit: Permits operation down to 7 deg C.

  - H. Mounting Base: Polyethylene.

- ACCESSORIES

  - Thermostat: To control compressor and evaporator fan, with the following features:

    - Compressor time delay.

    - 24-hour time control of system stop and start.

    - Liquid-crystal display indicating temperature, set-point temperature, time setting, operating mode, and fan speed.

    - Fan-speed selection, including auto setting.

    - System selection Heat-Off-Cool.

  - Automatic-reset timer to prevent rapid cycling of compressor.

  - Refrigerant Line Kits: Soft-annealed copper suction and liquid lines factory cleaned, dried, pressurized, and sealed; factory-insulated suction line with flared fittings at both ends. Refrigerant lines sizes as sized by equipment manufacturer. Provide filter drier and sight glass in each liquid line at each condensing unit.

- INSTALLATION

  - Install units level and plumb.

  - Install evaporator-fan components using manufacturer's standard mounting devices securely

Fasten to building structure.

  - Install roof-mounted compressor-condenser components on equipment supports specified in Division 7 Section "Roof Accessories." Anchor units to supports with removable, cadmium plated fasteners.

  - Install compressor-condenser components on restrained, spring isolators with a minimum static deflection of 25 mm. Refer to Division 15 Section "Mechanical Vibration Controls and Seismic Restraints."

  - Connect precharged refrigerant tubing to component's quick-connect fittings. Install tubing to allow access to unit.

- CONNECTIONS

  - Piping installation requirements are specified in other Division 15 Sections. Drawings indicate general arrangement of piping, fittings, and specialties.

  - Install piping adjacent to unit to allow service and maintenance.

  - Duct Connections: Duct installation requirements are specified in Division 15 Section "Metal Ducts." Drawings indicate the general arrangement of ducts. Connect supply and return ducts to split-system air-conditioning units with flexible duct connectors. Flexible duct connectors are specified in Division 15 Section "Duct Accessories."

  - Ground equipment according to Division 16 Section "Grounding and Bonding."

  - Electrical Connections: Comply with requirements in Division 16 Sections for power wiring, switches, and motor controls.

- FIELD QUALITY CONTROL

  - Installation Inspection: Engage a factory-authorized service representative to inspect field-assembled components and equipment installation, including piping and electrical connections, and to prepare a written report of inspection.

  - Leak Test: After installation, charge system and test for leaks. Repair leaks and retest until no leaks exist.

  - Operational Test: After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation. Remove malfunctioning units, replace with new components, and retest.

  - Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

- STARTUP SERVICE

  - Verify that units are installed and connected according to the Contract Documents.

  - Lubricate bearings, adjust belt tension, and change filters.

  - Perform startup checks according to manufacturer’s written instructions and do the following:

    - Fill out manufacturer’s checklists.

    - Check for unobstructed airflow over coils.

    - Check operation of condenser capacity-control device.

    - Verify that vibration isolation devices and flexible connectors dampen vibration transmission to structure.

QUALITY ASSURANCE

- Product Options: Drawings indicate size, profiles, and dimensional requirements of split system units and are based on the specific system indicated. Other manufacturers' systems with equal performance characteristics may be considered.

- Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, Article 100, by testing agency acceptable to authorities having jurisdiction, and marked for intended use.

- Energy-Efficiency Ratio: Equal to or greater than prescribed by ASHRAE/IESNA 90.1-2016 “Energy efficiency design of New Buildings except low-rise Residential Buildings.”

WARRANTY

- General Warranty: Special warranty specified in this Article shall not deprive Government of other rights Government may have under other provisions of the Contract Documents and shall be in addition to, and run concurrent with, other warranties made by Contractor under requirements of the Contract Documents.

- Special Warranty: Written warranty, executed by manufacturer agreeing to repair or replace components of split-system air-conditioning units that fail in materials or workmanship within specified warranty period.

- Warranty Period: The compressor shall have minimum five years warranty from date of substantial completion.

Provide price per unit as Main CAC, Consular CAC and Service CAC due the possibilities that not all units will be change.

The bidder shall provide lead time for ordering and an anticipated length of time for installation of each unit.

The bidder will provide all materials, equipment, labor, transportation and shipping necessary to complete the work. Work will be coordinated with the Facility Manager of the U.S. Consulate.

The U.S. Government cannot remit payment for services not yet performed. If the bidder needs partial payment upfront they should include the labor and materials separate on the bid so that the equipment can be purchased first and then labor paid for upon completion of the work.

Those bidders in the U.S. can ship the products to El Paso, TX and the Consulate will take care of the importation of the products. Those bidders in Mexico should plan on shipping the items directly to the Consulate or to their facilities which shall include the importation of the products.