The US Consulate General in Cd. Juarez is requesting quotes for 1 year preventive maintenance service for chillers. These services shall result in all systems being serviced under this agreement being in good operational condition when activated. Please send all your quotes in excel format no later than June 29th at 4:00 pm (central time) to this email address MaciasG@state.gov. No quotes will be considered after this date.

For U.S vendors make sure that you have a current DUNS number and that you are register in SAM otherwise your quote will not be considered. Mexican vendors have to quote in pesos unless they  have a U.S Dollars bank account in Mexico..

Please see equipment list below:

The Contractor shall provide all necessary managerial, administrative and direct labor personnel, as well as all transportation, equipment, tools, supplies and materials required to perform inspection, maintenance, and component replacement as required to maintain the systems in accordance with this work statement.  During the period of performance the Contractor shall provide:

The services of trained and qualified technicians to inspect, adjust, and perform scheduled preventive maintenance

The chillers shall be clean and in good operating condition upon completion of the service. The preventive maintenance service shall result in the parts of the system serviced being in a condition to operate efficiently and effectively.

The Contractor shall maintain work schedules.  The schedules shall take into consideration the hours that the staff can effectively perform their services without placing a burden on the security personnel of the Post. The Contractor shall deliver standard services between the hours of 8:00AM and 4:30 PM Monday through Friday. No work shall be performed on US Government and local holidays. Below is a list of the holidays.

| Date | Holiday | US/Local |
| --- | --- | --- |
| Jan 01 | New Year's Day | Am |
| Jan 18 | Birthday of Martin Luther King, Jr. | Am |
| Feb 15 | President's Day | Am |
| Mar 21 | Benito Juarez’s Birthday | Am |
| Mar 24 | Holy Thursday | Am |
| Mar 25 | Holy Friday | Am |
| May 01 | Mexican Labor Day | Am |
| May 05 | Anniversary of Battle of Puebla | Am |
| May 10 | Mother’s Day | Am |
| May 30 | Memorial Day | Am |
| Jul 04 | Independence Day | Am |
| Sep 05 | Labor Day | Am |
| Sep 16 | Mexican Independence Day | Am |
| Oct 10 | Columbus Day | Am |
| Nov 02 | All Soul’s Day | Am |
| Nov 11 | Veterans Day | Am |
| Nov 21 | Anniversary of Mexican Revolution | Am |
| Nov 24 | Thanksgiving Day | Am |
| Dec 26 | Christmas | Am |

I.    	GENERAL INFORMATION:

The US Consulate General Cd Juarez requires professional services and contractor cost proposals to perform preventive maintenance services of the facility’s Chillers Water Cooled.

II.	PROJECT REQUIREMENTS:

DESCRIPTION OF EQUIPMENT *:

*Please see attachment at the end of this sheet for more details

- 2 Rotary Screw Water Chiller, 220 tons, installed in 2008.

- 1 Modular Scroll Water Chiller, 115 KW, installed in 2008

III.	GENERAL REQUIREMENTS:

The Contractor under this SOW shall be responsible for labor, tools, and materials required to carry out all preventive maintenance as outlined in this SOW.

The Consulate has the following manuals:

-Chiller

-Controllers

-Master Starter

IV.	SCOPE OF WORK - - CHILLERS MAINTENANCE

Contractor shall provide all materials, supervision, labor, tools and equipment to perform preventive maintenance. All personnel working in the vicinity shall wear and /or use safety protection while all work is performed.  Any questions or injuries shall be brought to the attention of the Post Occupation Safety and Health Officer (POSHO) immediately.  Material Safety Data Sheets (MSDS) shall be provided by the Contractor for all HAZMAT materials.  Copies shall be provided to the COR for approval.

The Contractor shall inventory, supply and replace expendable parts (e.g., filters, belts, hoses, gaskets) that have become worn down due to wear and tear. The Contractor shall maintain a supply of expendable and common parts on site so that these are readily available for normal maintenance to include: hoses, belts, oil, chemicals, coolant, filters (Air, Fuel, Oil), grease, sealant, thermostat, fuses; in addition to the appropriate tools, testing equipment, safety shoes and apparel for technicians, personal protective equipment (hands, hearing, eye protection), MSDS, cleaning material and oil spill containment kits. The contractor should inventory the supply after each visit and order replacement supplies and have them delivered on site.  Maintenance materials shall be unused and are to be industry standard and intended for the task to be performed.  Parts are to be OEM approved.  Refrigerants are to meet the AHRI_Standard_700-2015 or most recent AHRI Standards.

Refrigerants, parts and maintenance materials delivered to the post are to be new and unused.  Reclaimed refrigerants are not to be delivered to posts.  Reclaimed refrigerants within post compounds are to be retained and stored and may be used if not contaminated. Refrigerants shall be stored in containers clearly indicating the refrigerant type.

SAFETY AND SPECIAL INSTRUCTIONS:

- Follow site safety procedures and supervisor’s instructions.

- Schedule outage with operating personnel.

- Use extreme caution when climbing access ladders.

- Perform applicable lockout/tag out steps of site safety procedures.

- Lockout and disconnect the main power before tightening the main supply lugs in order to avoid the hazard of electrical shock, which could result in serious personal injury or death.

- Record and report equipment damage or deficiencies.

- Review and follow the manufacturer’s O&M instructions.

- Record results in the equipment history log.

- Allow only qualified personnel to do maintenance work on this equipment.

- Record results in the equipment history log.

- Check manufacturer’s specifications for the maximum number of plugged tubes.

- Allow only qualified personnel to do maintenance work on this equipment.

CHILLERS

MAINTENANCE PROCEDURES:

Note to Statement of Work writer: The frequencies and tasks shown in this template SOW are for reference only.  The actual maintenance procedures will be determined by the manufacturer’s O&M recommendations.  These O&M recommendations may be obtained from the manufacturer or may already be within the post files.   The manufacturer’s maintenance recommendations are to be considered the minimum tasks to be provided and these tasks may be altered or increased depending upon the location of the post.

Additionally, it may be required the maintenance contractor shall obtain and keep at the post O&M binders provided by the manufacturers.  These binders will be placed in a location accessible to post personnel to review as needed.

Water Chillers:

Semi-Annually

- Check unit for proper operation.

- Check oil level; add oil as necessary.

- Check oil temperature.

- Check dehydrator or purge system; remove water if observed in sight.

- Run system control tests.

- Check refrigerant charge/level, add as necessary.

- Check compressor for excessive noise/vibration.

- Check sensor and mechanical safety limits; replace as necessary.

- Check oil heater operation.

- Leak check and repair leaks as needed.

- Check three-phase voltage and current balance.

- Clean area around equipment.

- Document all maintenance and cleaning procedures.

- Coils cleaning

- Fans lubrication

Annually

- Disconnect power source and lock out. Check electrical wiring and connections; tighten loose connections.

- Perform all check items in the Semi-Annual schedule.

- Clean dehydrator float valve.

- Perform spectrochemical analysis of compressor oil; replace oil as necessary.

- Replace oil filters and oil filter/driers and add oil as necessary.

- Inspect cooler and condenser tubes for leaks; clean screens as necessary.

- For dedicated PCC chillers the glycol level of the chill water is to be checked and adjusted to the percentage required by OBO Engineering Dept.

- Inspect utility vessel vent piping and safety relief valve; replace as necessary.

- Inspect/clean the economizer, gas line damper valve and actuator arm.

- Run an insulation test on the centrifugal motor.

- Clean area around equipment.

- Document all maintenance and cleaning procedures.

- Perform oil analysis on compressor lube oil.

- Perform refrigeration analysis.

- Perform vibration analysis

- Perform one refrigerant discharge (recovery) and reload for parts change.

- Megohm motor winding.

- Perform Eddy current testing and inspect tubes.

Motor Starter /Variable Frequency Drive:

MAINTENANCE PROCEDURES:

Annually:

- Vacuum dust and dirt from heat sink fins

- Check ventilation fans for proper operation and clean as needed.

- Check line voltage, motor & output phase balance

- Complete RCM Procedure CM-0002 (Qualitative Infrared Testing).

- Visually inspect for broken parts, contact arcing, or any evidence of overheating.

- Check motor nameplate for current rating and controller manufacturer’s recommended heater size (report discrepancy to supervisor).

- Check line and load connections for tightness (check manufacturer’s instructions for torque specifications).

- Check heater mounting screws for tightness.

- Check all control wiring connections for tightness.

- On units equipped with motor reversing capacity, check mechanical interlock.

- On units equipped with two-stage starting, check dash pots and timing controls for proper operation. Adjust as required.

- On units equipped with variable speed starters:

  - Record the VFD parameter settings using MCT-10

  - Confirm the VFD doors and covers are in place and properly closed.

  - Check tightness of connections to resistor bank.

  - Check resistor coils and plates for cracking, broken wires, mounting and signs of overheating. Clean as required.

  - Check tightness of connections to drum controller.

  - Check contacts of drum controller for arcing and overheating. Apply a thin film of lubricant to drum controller contacts and to rotating surfaces.

- Check starter contact connections by applying a thin film of black contact grease to line and load stabs, operate contacts and check surface contact.

- Lubricate all moving parts with proper lubricant.

- Clean interior of cabinet.

- Clean exterior of cabinet.

- Energize circuit and check operation of starter and any pilot lights. Replace as required.

Panel, Electronic Controls:

Annually

- Clean panel interior.

- Verify functionality of supported devices.

- Clean ventilation filter and fan (if applicable).

- Record and report equipment damage or deficiencies.

- Record results in the equipment history log

Bi-Annually

- Replace battery where applicable.